**120V/208V, 3-Phase in/3-Phase out:10KVA -60KVA**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **KVA** | | **10** | **20** | **30** | **40** | **50** | **60** |
| **RECTIFIER** | | | | | | | |
| INPUT VOLTAGE | | 120 / 208 VAC 3 Phase 4 Wire | | | | | |
| INPUT RANGE | | +/- 15% | | | | | |
| INPUT FREQUENCY | | 50 / 60 Hz +/- 7% | | | | | |
| INPUT POWER FACTOR | | 0.8 | | | | | |
| NORMAL INPUT CURRENT(A) | | 30 | 61 | 92 | 123 | 153 | 184 |
| MAXIMUM INPUT CURRENT(A) | | 38 | 76 | 115 | 153 | 192 | 230 |
| POWER WALK IN | | 0% - 100% : 20 sec | | | | | |
| EFFICIENCY | | 99% | | | | | |
| VOLTAGE REGULATION | | 1% | | | | | |
| CURRENT LIMIT(A) | | 46 | 92 | 138 | 184 | 230 | 276 |
| RIPPLE VOLTAGE | | 0.5% | | | | | |
| **BATTERY** | | | | | | | |
| BATTERY TYPE | | SEAL LEAD ACID / NiCd | | | | | |
| NO. OF CELLS | | 174 / 271 | | | | | |
| VOLTAGE RANGE | | 295 – 410VDC / 285-415VDC | | | | | |
| MAXIMUM CHARGE  CURRENT (ADC) | | 4 | 8 | 12 | 16 | 20 | 24 |
| BATTERY LOW VOLTAGE | | 320VDC / 305VDC | | | | | |
| BATTERY LOW STOP VOLTAGE | | 295VDC / 285VDC | | | | | |
| BOOST CHARGE | | 402VDC / 415VDC | | | | | |
| FLOAT CHARGE | | 390VDC / 410VDC | | | | | |
| **INVERTER** | | | | | | | |
| DC INPUT RANGE | | 285 – 420VDC | | | | | |
| WAVE FORM | | SINUSOID | | | | | |
| OUTPUT VOLTAGE | | 120 / 208 VAC 3 Phase 4 Wire | | | | | |
| OUTPUT POWER FACTOR | | 0.8 | | | | | |
| VOLTAGE REGULATION 100% UNBALANCE LOAD | | + / - 1 % | | | | | |
| FREQUENCY LOCK RANGE | | 45 – 55 Hz / 55 – 65 Hz | | | | | |
| OUTPUT FREQUENCY  (FREE RUNNING) | | 50 / 60 Hz + / - 0.1 Hz | | | | | |
| PHASE SHIFT UNDER  100% UNBALANCE LOAD | | 120 % + / - 0.5∘ | | | | | |
| THD (LINEAR LOAD) | | < 2 % | | | | | |
| OVERLOAD | <110% | CONTINUOUS | | | | | |
| 110 – 125% | 15 min | | | | | |
| 125 – 150% | 5 min | | | | | |
| > 150% | 30 sec | | | | | |
| EFFICIENCY (100% LOAD) | | 93% | 93% | 93% | 93.5% | 93.5% | 94% |
| MAXIMUM OUTPUT  PEAK CURRENT(A) | | 80 | 160 | 240 | 320 | 400 | 480 |
| **STATIC SWITCH** | | | | | | | |
| VOLTAGE RANGE | | 96 – 144 VAC (LINE TO NEUTRAL) | | | | | |
| FREQUENCY RANGE | | 45 – 55 Hz / 55 – 65 Hz | | | | | |
| EFFICIENCY | | 99.5% | | | | | |
| TRANSFER TIME: | | | | | | | |
| - MAINS -> INVERTER | | 0.2 ms | | | | | |
| - INVERTER -> MAINS | | 0.2 ms | | | | | |
| OVERLOAD | 100% | 30 sec | | | | | |
| 300% | 7 sec | | | | | |
| ISOLATION WITH OUTPUT | | YES | | | | | |
| **OVERALL CHARACTERISTICS** | | | | | | | |
| OVERALL EFFICIENCY | | 91% | 91% | 91% | 91.5% | 92% | 92% |
| OPERATING ENVIRONMENT: | | | | | | | |
| - TEMPERATURE | | 0 – 40℃ ( 32 – 104℉ ) | | | | | |
| - HUMIDITY | | 0% - 90% ( NON–CONDENSING ) | | | | | |
| - ALTITUDE | | <1500 M ABOVE SEA LEVEL | | | | | |
| MAXIMUM HEAT  DISSIPATION(KW) | | 0.65 | 1.3 | 1.9 | 2.6 | 3 | 3.5 |
| WEIGHT(Kg) (No Battery) | | 380 | 490 | 570 | 640 | 690 | 780 |
| DIMENSION: | | | | | | | |
| - HEIGHT(mm) | | 1600 | | | | | |
| - WIDTH(mm) | | 550 | | | | | |
| - DEPTH(mm) | | 800 | | | | | |
| - AUDIBLE NOISE | | < 65 dBA (AT 1 m) | | | | | |
| STANDARDS: | | | | | | | |
| - EN50091-1,-2 | | YES | | | | | |
| - FCC CLASS A | | YES | | | | | |
| PROTECTIONS: | | | | | | | |
| - SHORT CIRCUIT | | RECTIFIER, RESERVE, BYPASS NFB | | | | | |
| - LIGHTNING | | MOV | | | | | |
| - EMC FILTER | | INPUT & OUTPUT | | | | | |
| - GALVANIC ISOLATION | | BETWEEN INPUT & OUTPUT | | | | | |
| DATA DISPLAY BY LCD | | YES | | | | | |
| INDICATIONS & ALARMS: | | | | | | | |
| - LED,LCD,BUZZER | | YES | | | | | |
| DRY CONTACT | | YES | | | | | |
| BATTERY START | | YES | | | | | |

* All specifications mentioned above are subject to change without prior notice.