## 277V/480V, 3-Phase in/3-Phase out: 200KVA -500KVA

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **KVA** | **200** | **240** | **300** | **400** | **500** |
| **RECTIFIER** |
| INPUT VOLTAGE | 277 / 480 VAC 3 Phase 4 Wire |
| INPUT RANGE | +/- 15 % |
| INPUT FREQUENCY | 50 / 60 Hz +/- 7% |
| INPUT POWER FACTOR | 0.8 |
| NORMAL INPUT CURRENT(A) | 265 | 318 | 398 | 530 | 663 |
| MAXIMUM INPUT CURRENT(A) | 332 | 398 | 497 | 663 | 829 |
| POWER WALK IN | 15% - 100% : 15 sec |
| EFFICIENCY | 99% |
| VOLTAGE REGULATION | 1% |
| CURRENT LIMIT(A) | 398 | 477 | 597 | 796 | 995 |
| RIPPLE VOLTAGE | 0.5% |
| **BATTERY** |
| BATTERY TYPE | SEAL LEAD ACID / NiCd |
| NO. OF CELLS | 174 / 271 |
| VOLTAGE RANGE | 295 – 410VDC / 285-415VDC |
| MAXIMUM CHARGE CURRENT (ADC) | 80 | 96 | 120 | 160 | 200 |
| BATTERY LOW VOLTAGE | 320VDC / 305VDC |
| BATTERY LOW STOP VOLTAGE | 295VDC / 285VDC |
| BOOST CHARGE | 402VDC / 415VDC |
| FLOAT CHARGE | 390VDC / 410VDC |
| **INVERTER** |
| DC INPUT RANGE | 285 – 420VDC |
| WAVE FORM | SINUSOID |
| OUTPUT VOLTAGE | 277 / 480 V 3 Phase 4 Wire |
| OUTPUT POWER FACTOR | 0.8 |
| VOLTAGE REGULATION 100% UNBALANCE LOAD | + / - 1 % |
| FREQUENCY LOCK RANGE | 45 – 55 Hz / 55 – 65 Hz |
| OUTPUT FREQUENCY(FREE RUNNING) | 50 / 60 Hz + / - 0.1 Hz |
| PHASE DIFFERENCE WITHRESERVE INPUT | 120°+ / - 0.5° |
| THD (LINEAR LOAD) | < 5 % |
| OVERLOAD  | <110% | CONTINUOUS |
| 110 – 125% | 15 min |
| 125 – 150% | 5 min |
| > 150% | 30 sec |
| EFFICIENCY(100% LOAD) | 95% | 95% | 95% | 95% | 95% |
| MAXIMUM OUTPUT PEAK CURRENT(A) | 693 | 831 | 1039 | 1386 | 1733 |
| **STATIC SWITCH** |
| VOLTAGE RANGE | 222 – 332 VAC (LINE TO NEUTRAL) |
| FREQUENCY RANGE | 45 – 55 Hz / 55 – 65 Hz |
| EFFICIENCY | 99.5% |
| TRANSFER TIME: |
| - MAINS -> INVERTER | 0.2 ms |
| - INVERTER -> MAINS | 0.2 ms |
| OVERLOAD | 100% | 30 sec |
| 300% | 7 sec |
| ISOLATION WITH OUTPUT | YES |
| **OVERALL CHARACTERISTICS** |
| OVERALL EFFICIENCY | 93% | 93% | 93% | 93% | 93% |
| OPERATING ENVIRONMENT: |
| - TEMPERATURE | 0 - 40℃ ( 32 - 104℉ ) |
| - HUMIDITY | 0% - 90% ( NON–CONDENSING ) |
| - ALTITUDE | <1500 M ABOVE SEA LEVEL |
| MAXIMUM HEAT DISSIPATION(KW) | 11.5 | 13 | 16.3 | 23 | 29 |
| WEIGHT(Kg) (No Battery) | 2600 | 2850 | 3300 | 4100 | 4600 |
| DIMENSION: |
| - HEIGHT(mm) | 1600 |
| - WIDTH(mm) | 2200 | 3300 |
| - DEPTH(mm) | 800 |
| - AUDIBLE NOISE | < 68 dBA (AT 1 m) |
| STANDARDS: |
| -EN50091-1，2 | YES |
| -FCC CLASS A | YES |
| PROTECTIONS: |
| - SHORT CIRCUIT | RECTIFIER, RESERVE, BYPASS NFB |
| - LIGHTNING | MOV |
| - EMC FILTER | INPUT & OUTPUT |
| - GALVANIC ISOLATION | BETWEEN INPUT & OUTPUT |
| DATA DISPLAY BY LCD | YES |
| INDICATIONS & ALARMS: |
| - LED,LCD,BUZZER | YES |
| DRY CONTACT | YES |
| BATTERY START | YES |

* All specifications mentioned above are subject to change without prior notice.