| Model (LED Series) | AHA-203H | AHA-303H |
| --- | --- | --- |
| Input | Capacity | 2KVA/1400W | 3KVA/2100W |
|  | Phase | Single Phase |
|  | Nominal Voltage | 220Vac/110Vac |
|  | Voltage Range | 160-300Vac(70%-100%load),140-300Vac (50%-70% load), 118-300Vac (0%-50% load) |
|  | Frequency | 50Hz / 60Hz ±4Hz |
|  | Power Factor | ≧0.97 |
| Output | Voltage | 220VAC ± 2% (230V or 240V re-settable via LCD panel) 110V ± 2% (100V,115V or 120V re-settable via LCD panel ) |
|  | Frequency | Synchronized ( Line mode); 50Hz or 60Hz +/-0.5% (Battery mode) |
|  | Wave-form | True Sine wave |
|  | Distortion | Tower | ≦4% (linear load) ≦7% non-linear load) |
|  |  | Rack | 4% (linear load) , ≦7% non-linear load) |
|  | Overload Capacity | 105%~125% : 30 sec, UPS go bypass. >125% : UPS go Bypass immediately. Load reduce to 90%, UPS go back to inverter mode automatically. > 150%: 300ms,UPS shutdown. |
|  | Crest Ratio | 3: 1 |
| Battery | DC Voltage | 96V |
|  | Capacity | 12V / 7Ah X 8pcs |
|  | Back-up Time | ＞9min. | ＞5min. |
| Charger | Built-In /Option | 1Amp/8Amp |
|  | Recharging Time | 5 hrs to 90% |
| Bypass | Automatic | Overload or UPS fault |
|  | By setting | Voltage Range: 176~256V¡Ó20V (Re-settable via LCD panel) |
|  | Transfer Time | 0 ms( 2.5ms inverter to bypass) |
| Indicator | LCD (Series) | UPS status, I/P&O/P Voltage & Frequency ,Load %, Battery Voltage, Battery Capacity % ,Temperature, Model Spec., Event Log. LED: Normal (Green), Warning (Yellow), Fault (Red) |
|  | LED (Series) | Normal (Green), Bypass(Yellow), Battery Low (Yellow), Inverter (Green), Load% (5 LEDs), Battery % (5 LEDs), Fault(Red) |
| Outlet | Tower | NEMAx6pcs or IEC320x6pcs | NEMAx6pcs or IEC320x3+ TBx1 |
|  | Rack | NEMAx2+TBx1 or IEC320x4pcs | NEMAx2+TBx1 or IEC320x1+TBx1 |
| Audible Alarm | Battery Mode | Beeping every 4 seconds (re-settable) |
|  | Battery Low | Beeping every seconds |
|  | Overload | Beeping twice per second |
|  | Fault | Beeping Continuously |
| Interface | RS-232 Interface | UPSilon2000 monitoring software for Windows all, Unix systems and Novell. |
|  | Multi-Interface Slot | SNMP card, AS 400, Dry Contact, USB Selectable |
| Network | Surge Protection | RJ45 I/O port for Network or RJ 11 for Fax / Modem |
| Parallel | N/A |
| Environment | Temperature | 0~40℃; 32~104℉ |
|  | Humidity | 0-95% non-condensing |
|  | Acoustic Noise | ＜50 dBA ( at 1 M) |
| Physical | Weight (w/o Battery | 13.5kgs (Tower) 9.5 kgs ( (Rack) | 14.5kgs(Tower) 10.5kgs (Rack) |
|  | Weight (w/ Battery) | 34 kgs (Tower) N/A (Rack) | 35 kgs (Tower) N/A (Rack) |
|  | Dimension W*H*D | Tower | 200 x 352 x 450 mm |
|  |  | Rack | 440 x 88 x 465mm (Rack) |
|  | Color | White or Black |

- Tower Series: AHA-H, Rack Series: AHA-HR

- Rack Battery Bank (2U) is available for 8pcs (1 set) 12V/7Ah and 9pcs (3 sets) 12V/7Ah batteries.

- Specifications are subject to change without notice.